[image: image1.jpg]STABILIZED "

Renewable Lubric



Renewable Lubricants, Inc.

 476 Griggy Rd. NE, PO Box 474

Hartville, OH 44632-0474

Voice: 330.877.9982  Fax: 330.877.2266
www.renewablelube.com


[image: image2.png]/7 T\\N\
RENEWABLE
LUBRICANT Se




Bio- Synthetic Transformer Fluids 

"Biobased Lubricants that Perform Like Synthetics"

Bio- Synthetic Transformer Fluid is the first renewable and biodegradable dielectric fluid that is a pure synthetic hydrocarbon developed from renewable plant biobased crops. This allows it to be a true drop-in compatible replacement for petroleum based Transformer Fluids, exceeding ASTM D3487 and IEC 60296 specifications. It is a highly Stabilized grade, specifically engineered to deliver maximum resistance to oil degradation for prolonged high-performance operation. High viscosity index and dielectric strength allow product use over a wide temperature range and under heavy electric stress. Outstanding oxidation stability and high temperature properties are expected to extend transformer and fluid life and reduce maintenance over conventional petroleum transformer fluids.  It is compatible with petroleum hydrocarbons transformer fluids and transformer system components.
Bio- Synthetic Transformer Fluid meets the Environmental Protection Agency (EPA) 2013 Vessel General Permit (VGP) guidelines for Environmentally Acceptable Lubricants (EALs), and should be used in transformers where LOW TOXICITY, BIODEGRADABILITY and NON-BIOACCUMULATION properties are required.  It exceeds the acute toxicity (LC-50 / EC-50 >100 ppm) criteria adopted by the US Fish and Wildlife Service and the US EPA.  Bio-SynXtra Transformer Fluid is an ENVIRONMENTALLY ACCEPTED LUBRICANT (EAL) that is formulated from renewable biobased resources.  We believe Earth's environmental future rests in the use of renewable materials. 

 1 Based on previous studies and ASTM D-7373 calculated, Bio- Synthetic Transformer Fluid is Ultimate/Readily Biodegradable >60% within 28 days in ASTM D-5864 Aerobic Aquatic Biodegradation of Lubricants, and meets German Blue Angel CEC L-33-T-82 and CEC L-33-A-934 tests, for Readily Biodegradable >80% within 21 days. 

APPLICATIONS • Underground • Over Water • Mobile • Any Environmentally Sensitive Areas
TYPES • Power Transformers • Distribution Transformers
	Meets and exceeds ASTM D-3487 & IEC 60296
	Rigorous assurance of physical, electrical, and chemical properties and performance

	Excellent heat transfer characteristics
	Heat easily removed from core and windings

	Outstanding oxidation stability
	Extends transformer life and reduces maintenance

	Low Pour Point
	Can be used in very cold environments

	Exceptional dielectric strength (49Kv)
	Withstands high electric stress without breakdown

	High purity synthetic hydrocarbon

base oil
	High performance and drop-in compatibility for mineral oil replacement

	Low toxicity
	Reduces environmental impact in case of leaks or spills

	Biodegradable
	Safer for use in areas where an unintended release would impact local environment


STABILIZED by Renewable Lubricants™* is RLI’s trademark on their proprietary and patented anti-oxidant, anti-wear, and cold flow technology.  High Oleic Base Stock (HOBS) are agricultural base oils.  This Stabilized technology allows the HOBS to perform as a high-performance formula in high and low temperature applications, reducing oil thickening and deposits.

1 Ultimate Biodegradation (Pw1) within 28 days in ASTM D-5864 Aerobic Aquatic Biodegradation of Lubricants

* Trademark of Renewable Lubricants™, Inc. Copyright 1999 Renewable Lubricants, Inc.

Bio- Synthetic Transformer Fluid
	TYPICAL SPECIFICATIONS
	METHOD
	Bio-SynXtra Transformer Fluids
	Spec.

Requirements

	Specific Gravity @ 15.6°C

Viscosity @ 40°C

Viscosity @ 100°C

Viscosity @ 0°C

Viscosity Index
	ASTM D-287

ASTM D-445

ASTM D-445

ASTM D-445

ASTM D-2270
	0.88

11.7

3.0

64.2

184
	Report

12.0 (max)

3.0 (max)

76.0 (max)

90 (min)

	Pour Point

Flash Point (COC)

Aniline Point (COC)

Gassing Tendency, max, µL/min

Dissipation factor (power factor), at 60 Hz max, %:

25°C

100°C
	ASTM D-97

ASTM D-92

ASTM D-611

ASTM D-2300

ASTM D-924


	-57°C

178°C

113.4°C

-2.0

0.001

0.01
	Note 1

145°C (min)

63°C (min)

30 (max)

max

0.05

0.30

	Dielectric breakdown, kV

Dielectric breakdown, kV
	ASTM D-877

ASTM D-1816

     (1mm gap)

     (2 mm gap)
	49

31

48
	30 (min)

20 (min)

35 (min)

	Copper Corrosion Strip 3hr @ 100°C
	ASTM D-130
	1A
	DIN 51524 2(max) 

	Oxidation Stability (acid sludge)

72 Hours: %sludge by wt.

     Total acid no., mg KOH/g

164 hours: % sludge by wt.

     Total acid no., mg KOH/g


	ASTM D-2440


	0.1

0.3

0.2

0.4
	Max

<0.01

<0.01

<0.01

<0.01



	Oxidation Stability (Rotating Bomb), minutes
	ASTM D-2112
	>550
	195 min

	Corrosive Sulfur
	ASTM D-1275B
	Non-corrosive 
2d
	Non-corrosive

Tarnish Level

	Water content, ppm
	ASTM D-1533
	9
	35 max

	Neutralization Number, mg KOH/g
	ASTM D-974
	<0.01
	0.03 max

	PCM content, ppm
	ASTM D-4059
	ND
	ND

	Biodegradation Classification 
Environmentally Friendly 

USDA Biobased Tested 

Environmental Management System

	ASTM D-5864

ISO 15380

New Carbon

ISO 14001:1996
	Ultimate PW1

            yes

yes

yes


	Ultimate

 PW1

 yes
meets/exceeds >50%
yes




Availability
F.O.B. :Hartville, Ohio, USA
5 Gallon Pails

 Drums 











82294

   82296


